## Slide 1: GridLAB-D Turorial – Session 2
David P. Chassin
Summer 2016
dchassin@slac.stanford.edu
All registered trademarks are hereby recognized.
Powerflow Module

## Slide 2: Powerflow Overview
Powerflow: fundamental power system analysis tool.
  Problem statement: “For any system, given the voltages of the generators, the characteristics of power lines, and the voltage response of loads, determine the voltage magnitudes and angles at all nodes on the system.”
Solution allows for the calculation of derived quantities
  All line currents
  All power flows throughout the system

## Slide 3: Powerflow Overview
Transmission Systems
  Originally limited to transmission systems
  Many assumptions made in early flow solvers, e.g.,
    Positive sequence phase model
    Polynomial load response to voltage
Distribution Systems
  Stability & voltage sag wasn’t a problem  powerflow not done
  Initially based on simple circuit equivalents
  Sequential components used but found inappropriate.
  Recent work has focused on more complete modeling
    Full unbalanced 3-phase models are now the standard
    Composite load model is becoming more prevalent
    Distributed generation and voltage control a growing problem

## Slide 4: Distribution System Modeling
Traditionally analysis performed for transmission
  Distribution analysis growing in last 20 years
  Emerging technologies designed to operate in distribution
Distribution modeling similar to transmission modeling
  More detail in equipment models
  Single and double phase lines exist
  Distribution systems are often radial
  The R/X values in distribution are much higher
  Loads are unbalanced

## Slide 5: What Does “Unbalanced” Mean?
The voltage at the source is balanced:
The voltages downstream are unbalanced:

## Slide 6: Types of Distribution System Equipment
Very common in distribution systems:
  Overhead lines
  Underground cables
  Transformers
  Voltage regulators
  Shunt capacitors
Others that may be found:
  Switches
  Reclosers
  Fuses
  Lightning protection

## Slide 7: Transmission System

## Slide 8: Distribution System

## Slide 9: System Representations
Positive Sequence Model
  Assumed 3-phase balanced
  Single-phase equivalent models are used
  Performance advantage
Limits accuracy of model
  No phase-specific behavior
Three-phase Model
  Each phase explicit
  Model includes neutral
  Electromagnetic coupling
Allows accurate modeling
  Partial phase line topology
  Split-phase segments
  Single-phase loads
  Two-phase loads
  Phase-specific measurement, control design and actuation

## Slide 10: Modeling comparisons
Positive Sequence
Unbalanced
+
-

## Slide 11: Three-phase Unbalanced
4.0'
2.5'
4.5'
3.0'
a
b
c
n
24.0'
Physical System
Parameterized Values
Values for Numeric Simulation
Phase Conductor: 336,400 26/7
GMR = 0.0244 ft., Resistance = 0.306 Ω/mile, Diameter = 0.721 inch
Neutral Conductor: 4/0 6/1 ACSR
GMR = 0.00814 ft., Resistance = 0.592 Ω/mile, Diameter = 0.563 inch

## Slide 12: Overhead Line Code
Object Code
object overhead_line {
phases "BCN";
name ohl_632-645;
from node_632;
to load_645;
length 500 ft;
configuration line_config_603;
}
Configuration Code
object line_configuration {
name line_config_603;
conductor_B ohl_conductor_6030;
conductor_C ohl_conductor_6030;
conductor_N ohl_conductor_6030;
spacing line_spacing_505603;
}
// Phase Conductor for 603, 604, 605: 1/0 ACSR
object overhead_line_conductor {
name ohl_conductor_6030;
geometric_mean_radius 0.004460;
resistance 1.120000;
}
object line_spacing {
name line_spacing_505603;
distance_BC 7.0 ft;
distance_CN 5.657 ft;
distance_BN 5.0 ft;
}
B
C
N

## Slide 13: Underground Cables
Power conductors
Ground conductors

## Slide 14: Underground Cable Code
Object Code
object underground_line {
phases "AN";
name ugl684_652;
from node_684;
to load_652;
length 800;
configuration line_config_607;
}
Configuration Code
object line_configuration {
name line_config_607;
conductor_A ugl_conductor_6070;
conductor_N ugl_conductor_6070;
spacing line_spacing_520;
}
// Phase Conductor for 607: 1/0 AA,TS N: 1/0 Cu
object underground_line_conductor {
name ugl_conductor_6070;
outer_diameter 1.060000;
conductor_gmr 0.011100;
conductor_diameter 0.368000;
conductor_resistance 0.970000;
neutral_gmr 0.011100;
neutral_resistance 0.970000;
neutral_diameter 0.0640837;
neutral_strands 6.000000;
shield_gmr 0.000000;
shield_resistance 0.000000;
}
object line_spacing {
name line_spacing_520;
distance_AN 0.0833 ft;
}

## Slide 15: Service Transformers
Poletop
Padmount
Underground Vault

## Slide 16: Service Transformer Model
120V
120V
7,200V
240V

## Slide 17: Transformer Code
Object Code
object transformer {
groupid Distribution_Trans;
configuration tc100100B;
name f5_T21400253B;
from f5_L2691959;
to f5_X2691959B;
nominal_voltage 7200;
phases BS;
}
Configuration Code
object transformer_configuration {
name tc100100B;
connect_type SINGLE_PHASE_CENTER_TAPPED;
install_type POLETOP;
primary_voltage 7200.0;
secondary_voltage 120.0;
power_rating 100.0;
powerB_rating 100.0;
impedance 0.006+0.0136j;
// Only used in Wye-Wye and CTTF
impedance1 0.012+0.0204j;
impedance2 0.012+0.0204j;
shunt_impedance 259200+103680j;
}

## Slide 18: Voltage Regulators
Voltage regulators adjust the voltage on a branch
  Compensates for heavy (or light) loading
  Controls voltage drop (or rise) that results from load changes

## Slide 19: Voltage Regulators
Two winding auto transformers with a variable tap ratio
  Note: GridLAB-D represents voltage regulators as ideal transformers (no losses)

## Slide 20: Voltage Regulator Code
Object Code
object regulator {
name reg1501491;
phases "ABC";
from node_150;
to node_1491;
configuration regulator_config_15;
}
Configuration Code
object regulator_configuration {
name regulator_config_15;
connect_type WYE_WYE;
band_center 120.000;
band_width 2.0;
time_delay 30.0;
raise_taps 16;
lower_taps 16;
current_transducer_ratio 700;
power_transducer_ratio 20;
compensator_r_setting_A 3.0;
compensator_x_setting_A 7.5;
compensator_r_setting_B 3.0;
compensator_x_setting_B 7.5;
compensator_r_setting_C 3.0;
compensator_x_setting_C 7.5;
CT_phase "ABC";
PT_phase "ABC";
regulation 0.10;
Type A;
tap_pos_A 7;
tap_pos_B 7;
tap_pos_C 7;
Control MANUAL; // OUTPUT_VOLTAGE, // LINE_DROP_COMP or REMOTE NODE
}

## Slide 21: Shunt Capacitors

## Slide 22: Capacitor Code
Object Code
object capacitor {
phases ABCN;
name CAP1;
pt_phase ABCN;
parent 675;
phases_connected ABCN;
control VOLT;
voltage_set_high 2700.0;
voltage_set_low 2250.0;
capacitor_A 0.10 MVAr;
capacitor_B 0.10 MVAr;
capacitor_C 0.10 MVAr;
control_level INDIVIDUAL;
time_delay 300.0;
dwell_time 0.0;
switchA CLOSED;
switchB CLOSED;
switchC CLOSED;
nominal_voltage 2401.7771;
}
  Control modes available: MANUAL, VOLT, VAR, VARVOLT and CURRENT
  pt_phase determines the phases to monitor for controls
  nominal_voltage determines the impedance value
  control_level may also be BANK
  lockout_time allows minimum time between control operations
  remote_sense/remote_sense_B may be used for remote sensing operations

## Slide 23: End Use Load Modeling
End use loads can be modeled in a variety of ways depending on the purpose.
  Time-invariant load models (ZIP models)
  Time-variant load models
  Physical/performance load models (motor/power electronics)
  Multi-state/control response load models
  Dynamic response models (Deltamode)
Note: Most of the loads in GridLAB-D are represented in the residential module, but the basic theory is described here.

## Slide 24: Time-invariant load models
Used for static power flow solution
  Used for capacity planning: peak load is examined
  Traditional ZIP load model

## Slide 25: ZIP Load Model for 13W CFL
 | ZIP Values |  |  |  |  | 
 | Z_% | I_% | P_% | Z_pf | I_pf | P_pf
CFL-13W | 40.85% | 0.67% | 58.49% | -0.88 | 0.42 | -0.78

## Slide 26: Time-variant load models
Often referred to as load profiles or load shapes
  Can be power or ZIP values that change with time
  Often comes from measured data with aggregated value

## Slide 27: ZIP Load Code
Object Code
object ZIPload {
groupid plugload;
base_power plug1*2.828958;
power_fraction 0.100000;
impedance_fraction 0.800000;
current_fraction 0.100000;
power_pf 0.950000;
current_pf 0.950000;
impedance_pf 0.950000;
};
Schedule Code
schedule plug1 {
0-23 0 * * * 0.1605;
24-59 0 * * * 0.1381;
0-30 1 * * * 0.1297;
31-59 1 * * * 0.1289;
0-34 2 * * * 0.1254;
35-59 2 * * * 0.1301;
0-29 3 * * * 0.1255;
30-59 3 * * * 0.1276;
0-18 4 * * * 0.1292;
19-44 4 * * * 0.1399;
45-59 4 * * * 0.1422;
0-14 5 * * * 0.1438;
15-35 5 * * * 0.1621;
36-59 5 * * * 0.1806;
0-14 6 * * * 0.1981;
...
}

## Slide 28: Physical Load Models
Load models based on physical process
  HVAC, energy storage, thermal processes, etc.
  Usually time-variant model
  Can be significantly more complicated than ZIP models
  Usually cannot be modeled using a single LTI model
  Provide detail necessary to consider actual load behavior

## Slide 29: Physical Load Model – Residential HVAC

## Slide 30: Multi-State Physical Load Models
Allow for more than one state of operation
  Usually requires a control system to govern state dynamics
  Almost always results in non-LTI model
  Necessary for modern appliances & demand response
HVAC systems are a good example:
  State 1: Off
  State 2: Cooling
  State 3: Heating
  State 4: Auxiliary Heating

## Slide 31: Multi-State Physical Load Models
From State | To State | Transition Rule
1 | 2 | Tair > (Thigh + DBhigh)
1 | 3 | Tair < (Tlow – DBlow)
1 | 4 | Tair < (Tlow – DBlow) & Tout < Taux
2 | 1 | Tair < (Thigh – DBhigh)
3 | 1 | Tair > (Tlow + DBlow)
3 | 4 | Tout < Taux
4 | 1 | Tair > (Tlow + DBlow)

## Slide 32: Multi-State Physical Load Models

## Slide 33: Distribution System
Given the source voltage and end use load, determine the voltage magnitude and angle at every node in the system.
Power Flow Solution Methods

## Slide 34: Two methods available
Forward/Backward Sweep method
  Fast, efficient, and robust to initial conditions
  Cannot solve meshed systems
  Reference:
    W. H. Kersting, “Distribution System Modeling and Analysis, 2nd Edition”, CRC Press, 2007.
Newton-Raphson Method
  Can solve meshed systems
  Requires Jacobian
  Fast converges for good initial values, otherwise, may fail to converge
  References:
    P. A. N. Garcia, J. L. R. Pereira, S. Carneiro Jr., V. M. Da Costa, and N. Martins, “Three-Phase Power Flow Calculations using the Current Injection Method”, IEEE Transaction on Power Systems, vol. 15, issue 4, pp. 508-514, May 2000.
    Araujo, L.R.; Penido, D.R.R.; Carneiro, S.; Pereira, J.L.R.; Garcia, P.A.N., “A Comparative Study on the Performance of TCIM Full Newton versus Backward-Forward Power Flow Methods for Large Distribution Systems”, in Proc. 2006 IEEE PES Power Systems Conference and Exposition, pp. 522-526.

## Slide 35: Forward/Backward Sweep (FBS) method
FBS method also called ladder solver
  Among earliest methods used for unbalanced power flow.
  Very efficient algorithm for radial systems
  Cannot solve looped systems
  Some components may make system appear non-radial
    Backflows from DG are allowed
    Lateral switching may reverse currents
Overall very good solution method, but has known limitations
  Deltamode and reliability modules don’t support FBS solver

## Slide 36: Forward/Backward Sweep Example

## Slide 37: Backward Sweep
Starting with an assumed or known voltage and calculate the current to each load in the system
Node 634 load:
Phase a: 160 kW; 110 kVar
Phase b: 120 kW; 90 kVar
Phase c: 120 kW; 90 kVar
Assume:
Phase Va: +2401 +0j
Phase Vb: -1200 -2080j
Phase Vc: -1200 +2080j
Yields:
Ia= +66.6 -45.8j
Ib= -57.4 -24.6j
Ic= +7.5 +62.0j
Given: I=(S/V)*

## Slide 38: Backward Sweep
Sum the currents at each node in the system until the current at the source is determined.
Ia= +66.6 -45.8j
Ib= -57.4 -24.6j
Ic= +7.5 +62.0j

## Slide 39: Forward Sweep
Use currents to determine voltage drops on segments
  Voltage drop depends on load of other phases  complete per phase calculation must be used

## Slide 40: Recalculate Load
Recalculate new current draw using new voltages for each load and perform another sweep

## Slide 41: Newton-Raphson Method
Developed for positive sequence transmission analysis
  Adapted for 3-phase unbalanced distribution analysis
  Based on the real/reactive power injections at each node
  Power injections used to update voltage magnitude and angle
  Requires the calculation and inversion of a Jacobian
  Computationally intensive
GridLAB-D implementation features
  Automatically constructs/updates Jacobian from models
  Uses previous results as initial condition  fast convergence

## Slide 42: Newton-Raphson Method
Pi the real power injection at node i
Qi the reactive power injection at node i
Gik real portion of the admittance between node i and k
Bik imaginary portion of the admittance between node i and k
Vi the voltage magnitude at node i
i the voltage angle at node i

## Slide 43: Newton-Raphson Example (Transmission Level Example)

## Slide 44: Newton Raphson Procedure

## Slide 45: Newton Raphson Procedure

## Slide 46: N-R Power Flow Results

## Slide 47: Newton-Raphson Method (TCIM)
Instead of voltage magnitudes and angles, TCIM calculates the real and reactive components
Voltage magnitudes and angle are then calculated from the components

## Slide 48: Time-series Simulations
Time series simulations necessary for certain analyses
  Allows focus on “non-peak capacity” conditions
  Simulations are series of steady-state power flow solutions
Commonly called “quasi-steady” simulation
  Differ from dynamic or electromagnetic simulations
Time (t)
State (x)
x
t

## Slide 49: Modified IEEE 13 Node Test System

## Slide 50: Time-series Simulations (II)

## Slide 51: How does it work?
Distribution system handled as network (nodes & links)
Forward-Backward Sweep (FBS)
  Voltage (nodes) and current (links) passed in sweeps
  Sweeps repeated each time step until zero voltage “error”
Newton-Raphson (NR)
  Admittance matrix built from links
  Used to calculate node voltages given current injections
  Iterations performed by SuperLU until zero voltage “error”
Iterations by GridLAB-D handles control algorithms

## Slide 52: Powerflow module directives
Preferred method depends on application
  As implemented, FBS is faster
  As implemented, NR handles meshed systems, reconfiguration algorithms, and reliability
Both methods support all objects in all other modules
  Exceptions for FBS:
    Reconfiguration, reliability, and deltamode (dynamics).
module powerflow {
solver_method FBS; // or NR; GS is deprecated as V3.0
default_maximum_voltage_error 1e-6; // defines convergence criteria
NR_iteration_limit 50; // max SuperLU iterations per GLD iteration
NR_superLU_procs 1; // max processors assigned to SuperLU
}

## Slide 53: Objects in Powerflow Module
Two main object types: node and link
  Most powerflow objects inherit properties from node and link
Library objects
  Specify configurations that are used multiple times
    line_configuration
    line_spacing
    transformer_configuration
    regulator_configuration
  Provide “library” values to compute model parameters
  Not used directly in constructing solutions

## Slide 54: Abstract node and link objects
FBS calculation done at level of node and link objects
  Node Objects
  Link Objects
  Capacitor
  Load
  Meter/triplex_meter
  PQLoad
  Substation
  Fuse
  Switch_object
  Relay
  Recloser
  Sectionalizer
  Billdump
  Voltdump
  Motor (experimental)
  Frequency_gen
  Volt_var_control
  Currdump
  Emissions
  Overhead_line
  Underground_line
  Triplex_line
  Series_reactor
  Regulator
  Transformer

## Slide 55: Node objects
class node {
  complex voltage_A[V]; // used to initialize voltage solution
  complex voltage_B[V]; // then tracks voltage over time
  complex voltage_C[V];
  complex voltage_AB[V]; // used for delta voltage connections
  complex voltage_BC[V];
  complex voltage_CA[V];
  complex current_A[A];
  complex current_B[A];
  complex current_C[A];
  complex power_A[W];
  complex power_B[W];
  complex power_C[W];
  complex shunt_A[S];
  complex shunt_B[S];
  complex shunt_C[S];
  set phases; // A,B,C,D,N or S
  enum bustype; // PQ (default), PV, SWING
  double maximum_voltage_error;
}

## Slide 56: Loads
class load {
// also inherits properties from node object complex constant_impedance_A[Ohm]; // Z_A
complex constant_impedance_B[Ohm]; // Z_B
complex constant_impedance_C[Ohm]; // Z_C complex constant_current_A[A]; // I_A
complex constant_current_B[A]; // I_B
complex constant_current_C[A]; // I_C
complex constant_power_A[VA]; // P_A complex constant_power_B[VA]; // P_B
complex constant_power_C[VA]; // P_C
}
May be used to define general purpose load classes
  Residential, industrial, commercial, agricultural, mixed class

## Slide 57: Meters
Meters are the interaction point between the powerflow module and the commercial and generator modules (often used on loads)
class meter {
// also inherits properties from node object
double measured_real_energy[Wh];
double measured_reactive_energy[Vah];
complex measured_power[VA]; // also measured_power_A, _B, _C
double measured_real_power[W];
double measured_reactive_power[W];
complex measured_voltage_A[V];
complex measured_voltage_B[V];
complex measured_voltage_C[V];
complex measured_current_A[A];
complex measured_current_B[A];
complex measured_current_C[A];
}

## Slide 58: Triplex meters
Triplex meters are interaction point between powerflow module and residential module
  Billing information may be extracted using bill_mode.
Class triplex_meter {
// also inherits properties from node object
double measured_energy[Wh];
double measured_power[W];
double measured_real_power[W];
double measured_reactive_power[W];
complex measured_voltage_1[V];
complex measured_voltage_2[V];
complex measured_voltage_N[V];
complex measured_current_1[A];
complex measured_current_2[A];
complex measured_current_N[A];
}

## Slide 59: Link objects
No “generic” link object (unlike node)
  underground_line and triplex_line follow the same format
  “to” and “from” define the two nodes that the link connects
  configuration is defined by a separate “library” object
  configuration and length determine all relevant matrices for powerflow calculations
class overhead_line {
// inherited from link objects
char64 name;
set phases; // A,B,C,D,N or S
object from;
object to;
// Specific to line objects
double length[ft];
object configuration;
}

## Slide 60: Lines
All lines may be specified directly using a z-matrix (not the best way to do it)
  Matrix symmetry checks are not performed
  Negative resistance gives a warning but are accepted
class line_configuration {
complex z11[Ohm/mile]; // line impedances
complex z12[Ohm/mile];
complex z13[Ohm/mile];
complex z21[Ohm/mile];
complex z22[Ohm/mile];
complex z23[Ohm/mile];
complex z31[Ohm/mile];
complex z32[Ohm/mile];
complex z33[Ohm/mile];
double c11[nF/mile]; // shunt capacitances
double c12[nF/mile];
double c13[nF/mile];
// etc.
}

## Slide 61: Transformers
Specific transformer parameters are in library object
  Parameters are in transformer_configuration
  Allows definition of many transformer types
class transformer {
// inherits from link object object from;
object to;
double power_in[W]; double power_out[W]; object configuration;
}

## Slide 62: Transformer configurations
class transformer_configuration {
enumeration connection_type;
enumeration install_type;
// continued ...
}
Connection types
  WYE_WYE
  DELTA_DELTA
  DELTA_GWYE
  SINGLE_PHASE
  SINGLE_PHASE_CENTER_TAPPED
Install types
  POLETOP
  PADMOUNT
  VAULT

## Slide 63: Transformer configuration (cont.)
object transformer_configuration {
// ... continued
double primary_voltage[V];
double secondary_voltage[V];
double power_rating[kVA];
double power_rating_A[kVA];
double power_rating_B[kVA];
double power_rating_C[kVA];
double resistance[pu.Ohm];
double reactance[pu.Ohm];
complex impedance[pu.Ohm];
complex impedance1[pu.Ohm]; // specifies individual
complex impedance2[pu.Ohm]; // center taps impedances
complex shunt_impedance[pu.Ohm]; // center tap and
// wye-wye shunt loss
}

## Slide 64: Regulators
Regulator parameter definitions
  Specified by regulator_configuration
  tap_A etc. specify initial tap positions or manual control
sense_node used only for specific modes
  Specifies remote locations to observe voltage
class regulator {
// inherited from link object
object configuration;
int16 tap_A;
int16 tap_B;
int16 tap_C;
object sense_node;
}

## Slide 65: Objects in powerflow Module
class regulator_configuration {
enumeration connect_type; //WYE_WYE is the only operational type at this time
double band_center[V];
double band_width[V];
double time_delay[s];
double dwell_time[s];
double raise_taps;
double lower_taps;
double current_transducer_ratio[pu]; // used in line drop compensation
double power_transducer_ratio[pu];
double compensator_r_setting_A[V];
double compensator_r_setting_B[V];
double compensator_r_setting_C[V];
double compensator_x_setting_A[V];
double compensator_x_setting_B[V];
double compensator_x_setting_C[V]; // used in line drop compensation mode
string CT_phase;
string PT_phase;
double regulation;
enumeration control; // MANUAL, OUTPUT_VOLTAGE, LINE_DROP_COMP, or REMOTE_NODE
enumeration type; // A or B
enumeration control_level; // INDIVIDUAL or BANK
int tap_pos_A;
int tap_pos_B;
int tap_pos_C;
}

## Slide 66: Node-to-Node Connection
Connected via a link object
  object overhead_line {
  name ovl_12;
  phases "ABCD";
  from node_1; // name or class:id
  to node_2; // name or class:id
  length 2000;
  configuration lineconfig_300;
  }
Connected via parent/child relationship (length = 0)
  object node {
  name node_2;
  phases "ABCD";
  parent node_1;
  }

## Slide 67: Feeder Example
IEEE 4 Node Feeder
  Presented as a system of nodes and links
Use FBS and NR method to solve
  Compare the solutions

## Slide 68: Powerflow Output
3-ph voltage at each node, including inherited objects
  Power/current in/out
    Each phase
    Each link,
    Includes inherited objects
  Additional information available for specific objects,
    Tap positions
    Switch states
  Log of events
    Output to KML if specified

## Slide 69: Sample Static Powerflow Output
Load object: (node)
Transformer object: (link)
Name | constant_power_A | constant_power_B | constant_power_C | voltage_A | voltage_B | voltage_C
(load_11) (#11) | 1.8e+006+871780j W | 1.8e+006+871780j W | 1.8e+006+871780j W | 1918.94-271.698j V | -1266.24-1576.4j V | -697.555+1873.95j V
Name | configuration | status | From | to | power_in | power_out | phases
(transformer_8) (#8) | transformer_config_4 | CLOSED | node7 | node9 | +7.17672e+006 W | +6.81855e+006 W | ABCD

## Slide 70: Time-Series Powerflow Output
Time-series gives a solution for each time step
  Series of .xml files is not practical:
    1 year at 1 minute resolution yields 525,600 solutions
Use recorders to output desired values to .csv files.
These can then be post processed or plotted.

## Slide 71: Exercise 4.1
Load one IEEE 4-node test feeder, run it, and examine the output file.
Run the feeder with different transformer configurations and note the effects.

## Slide 72: Exercise 4.2
Load the IEEE 37-node test feeder, which will be used in other exercises.
There is a missing line. Find the missing line and fix the model to include the line.
Replace this line with a Delta-Delta transformer.
Connect an additional load via a node-to-node connection (e.g., without a link object).

## Slide 73: Exercise 4.3
Load the IEEE 13-node test feeder, with building loads already attached.
Examine the interface between the powerflow module and the residential module at the triplex meter objects.